## Instructions
Vendor Response Workbook — iWin-Type BIPV v3
Purpose
Use this workbook to collect vendor responses, review evidence quality, and score closure quality against the iWin pre-design pack.
House rules
1. Every response must reference a revision-controlled document, drawing, report, or procedure where applicable.
2. Mark each response as contractual or informational.
3. Priority A items and all Knockout = Y rows should be treated as mandatory for credible technical screening.
4. Use the Questionnaire sheet for the raw response, Closure_Map to track blocked assumptions/design rows, and Scoring for the internal review.
Sheet guide
Questionnaire — vendor-facing response matrix with blank response columns.
Closure_Map — maps open assumptions and design-envelope rows to the questions that close them.
Scoring — internal weighted review sheet with knockout logic.

## Questionnaire
ID | Section | Priority | Knockout | Question | Why it matters | Requested response format | Evidence requested | Related design rows | Related assumptions | Vendor response | Document reference | Revision/date | Contractual or informational | Received | Reviewer notes
DOC-01 | Document control | A | Y | Provide the current commercial product datasheet and the full document list that governs the offered revision. | Prevents mixing pilot, concept, and current commercial data. | PDF datasheet + document register | Datasheet, document list, revision status, issue dates | S01,S02,S16,S18 | A03
DOC-02 | Document control | A | Y | State whether the offered product revision is identical to the one represented on the public product page and in the pilot-validation literature. If not, list all material differences. | Stops false transfer of pilot or marketing claims onto a different build state. | Narrative + delta table | Revision-to-revision change log, superseded part list | S01,S02,S10 | A03,A04
DOC-03 | Document control | B | N | Provide the applicable installation manual, electrical manual, maintenance manual, and troubleshooting guide. | Closes serviceability and handover scope early. | PDF set | Manuals with revision/date | S18,S19 | A07,A10
DOC-04 | Document control | B | N | Name the technical owner for electrical design, façade integration, controls, and warranty decisions. | Needed for fast closure of cross-disciplinary items. | Contact table | Responsible person, role, email, authority boundary | S18,S19
DOC-05 | Document control | B | N | List all third-party components embedded in the offered configuration. | Needed for connector, cable, electronics, and actuator traceability. | BOM summary table | Manufacturer, part number, function, revision, country of origin | S12,S13,S14,S15 | A09
ARC-01 | Architecture and section | A | Y | Provide a section drawing showing outer lite, cavity/chamber, PV blind location, actuator location, feedthrough route, and replaceable boundaries. | This is the master closure item for thermal path, moisture path, service boundary, and electrical exits. | Section drawing | Drawing PDF/DWG with dimensions, callouts, revision/date | S01,S02,S13,S19 | A04,A05,A07
ARC-02 | Architecture and section | A | Y | State whether the PV blind sits in the main IGU cavity or in a dedicated chamber, and quantify cavity/chamber dimensions and gas/fill assumptions. | Directly affects temperature, condensation risk, and optical assumptions. | Structured table | Section dimensions, gas or venting description, spacer concept | S02,S11,S17 | A04
ARC-03 | Architecture and section | A | Y | Define the smallest independently replaceable unit for glazing, blind cassette, actuator, local electronics, and feedthrough hardware. | Needed to estimate downtime, spares, and façade intervention size. | Boundary table + diagram | Replacement procedure excerpt, service drawing | S19 | A07,A10
ARC-04 | Architecture and section | A | Y | State whether actuation is local per window, per cassette, per mullion group, or centralized across multiple windows. | Changes wiring, diagnostics, controls, and common-cause failure risk. | Architecture note + block diagram | Control architecture drawing, power budget | S12,S19 | A06
ARC-05 | Architecture and section | B | N | List façade integration constraints that materially affect performance or qualification (orientation, mullion depth, cavity spacing, frame material, installation tolerances). | Needed so yield and thermal claims are not detached from the install context. | Constraint table | Installation manual extracts, tolerance table | S02,S11,S17
ARC-06 | Architecture and section | B | N | Describe drainage, condensation, and moisture-management paths relevant to the blind, feedthrough, and frame interfaces. | Moisture path discipline is central in enclosed moving PV assemblies. | Narrative + detail sketch | Detail drawing, seal concept, inspection points | S13,S19 | A05,A10
ELE-01 | PV element and ratings | A | Y | Provide the electrical datasheet for one offered window unit: Pmax, Voc, Vmp, Isc, Imp, temperature coefficients, NOCT or equivalent, maximum system voltage, and polarity conventions. | No architecture screening is credible without the actual unit electrical envelope. | Datasheet table | Datasheet or qualified test report | S03,S04,S05,S16 | A03
ELE-02 | PV element and ratings | A | Y | State the actual PV technology and stack used in the offered product revision, including chemistry/family, active-area fraction, and any technology-dependent constraints. | The public clue 'thin-film' is insufficient for qualification, temperature, and degradation analysis. | Technology declaration | Manufacturer statement, cell/module datasheet, qualification path | S08,S09,S10 | A03
ELE-03 | PV element and ratings | A | Y | Provide the internal electrical subdivision of one unit: number of slats, active slats, substrings/strings per slat or per zone, and the interconnection diagram. | This is required for mismatch modeling and fault localization. | Interconnect drawing + table | Schematic, harness drawing, string map | S03,S04,S16
ELE-04 | PV element and ratings | A | Y | Provide the bypass topology and exact allocation: one diode per string, per substring, shared between strings, or another arrangement. | Bypass allocation is a first-order performance and hot-spot risk variable for this product class. | Topology note + schematic | Schematic, part numbers, diode ratings | S03,S04,S09
ELE-05 | PV element and ratings | A | Y | Provide representative I–V and P–V curves for the actual product at multiple irradiance and temperature points, including at least one partial-shading or angle-dependent case. | Needed to validate MPPT compatibility and mismatch assumptions. | Plots + raw numeric table | Test report, CSV, model basis | S05,S16,S17
ELE-06 | PV element and ratings | A | Y | State the allowed series and parallel aggregation limits and the design rule used to derive them. | Required for Voc,max/Isc,max and for preventing unsafe or nonfunctional stringing. | Aggregation rules table | Application note or electrical manual | S03,S04,S05
ELE-07 | PV element and ratings | A | Y | State the required downstream power-conversion architecture: direct stringing, optimizer-based, modular AC, or other. Identify any architectures that are explicitly not allowed. | Avoids wasting time on architectures the product cannot support. | Architecture note | Design manual extract, supported topologies list | S05,S12
ELE-08 | PV element and ratings | A | Y | Define the disconnect and isolation boundary for safe maintenance, fault finding, and unit replacement. | This is a go/no-go serviceability and safety item. | Single-line + service note | Single-line diagram, isolation procedure, lockout note | S06,S18,S19 | A07
ELE-09 | PV element and ratings | A | Y | State the earthing, insulation monitoring, and ground-fault or leakage-fault handling concept expected by the vendor. | Needed to match inverter/PCE choice and site safety design. | Protection concept note | Electrical manual, example single-line, monitoring requirements | S07,S12
ELE-10 | PV element and ratings | A | Y | Provide frame-feedthrough details: electrical rating, dielectric path, creepage/clearance basis, strain relief, bend control, and environmental sealing. | Feedthroughs are one of the highest-risk hidden interfaces in the product. | Detail drawing + component table | Feedthrough drawing, qualification/test basis, part numbers | S13,S14,S15 | A05,A09
ELE-11 | PV element and ratings | A | Y | Provide the approved DC connector family, mating restrictions, and prohibited connector combinations. | Connector incompatibility is a recurrent PV failure source and must be controlled contractually. | Connector schedule | Part numbers, ratings, installation instructions | S14 | A09
ELE-12 | PV element and ratings | A | Y | Provide the approved cable class, insulation type, temperature rating, voltage rating, minimum bend radius, and route limitations near moving parts or warm frame zones. | Needed to prevent hidden fatigue and thermal derating errors. | Cable schedule | Cable datasheet, route note, installation limits | S15,S19 | A09
ELE-13 | PV element and ratings | B | N | State whether reverse-current protection, string fusing, SPDs, and surge/ESD measures are required or prohibited at the unit or group level. | Clarifies BOS responsibilities and avoids unsafe default assumptions. | Protection responsibility matrix | Application note, single-line examples | S06,S07
ELE-14 | PV element and ratings | B | N | Provide expected electrical signatures for common faults such as bypass failure, open substring, loss of isolation, or wrong polarity after replacement. | Improves commissioning scripts and remote diagnostics. | Fault-signature table | Diagnostic guide, event mapping, test data | S18,S19,S20
CTL-01 | Controls and interfaces | A | Y | Provide the controls architecture: local controller location, communication protocol(s), power supply requirements, and BMS/SCADA integration boundary. | Controls determine both optical behavior and operational maintainability. | Block diagram + I/O summary | Controls architecture drawing, protocol spec | S12,S18,S19 | A06
CTL-02 | Controls and interfaces | A | Y | Provide the point list for all measured and commanded signals: slat angle, actuator status, fault state, temperature, irradiance/light, occupancy, and communication health. | Needed to verify observability and close the monitoring baseline. | Point list table | BMS/controls I/O list, Modbus/BACnet map | S18,S19 | A08
CTL-03 | Controls and interfaces | A | Y | Provide actuator electrical and mechanical data: voltage, current, inrush, torque margin, duty cycle, travel time, angle resolution, and rated lifetime cycles. | This is required for power sizing and reliability review. | Actuator datasheet table | Actuator datasheet, qualification report | S12,S19 | A06
CTL-04 | Controls and interfaces | A | Y | State the angle-feedback method and the guaranteed error between commanded angle and actual angle over life and temperature. | Angle mismatch directly degrades glare control, heat gain, and energy yield. | Accuracy specification | Control spec, test report | S18,S19
CTL-05 | Controls and interfaces | A | Y | Define fail-safe behavior for loss of sensor, loss of communications, power interruption, controller reboot, and actuator stall. | Fail-safe state is a design requirement, not a commissioning detail. | State table | Functional safety note, controls manual | S18,S19
CTL-06 | Controls and interfaces | B | N | Describe manual override, local recovery, and post-fault restart behavior. | Needed for facility operations and troubleshooting. | Procedure note | Service manual, operator guide | S19
CTL-07 | Controls and interfaces | B | N | Provide the alarm/event dictionary with severity classes and timestamp behavior. | Makes remote fault localization realistic. | Alarm list | Alarm dictionary, sample logs | S18,S19
CTL-08 | Controls and interfaces | B | N | Provide firmware-update method, rollback method, and version traceability rules. | Reduces configuration drift and upgrade risk in façade-integrated assets. | Software maintenance note | Firmware management procedure | S19
THM-01 | Thermal and qualification | A | Y | Provide measured or modeled temperatures for slat/cell, cavity/chamber air, local electronics, and frame-exit zones under representative summer and winter conditions. | Thermal behavior is a first-order design unknown for glazing-integrated PV blinds. | Plots + numeric table | Thermal report, CFD or test report, measurement basis | S11,S16,S17 | A04,A08
THM-02 | Thermal and qualification | A | Y | Provide declared operating limits, derating behavior, and protective thresholds for PV, electronics, and actuators. | Needed to define control limits and abnormal-condition handling. | Limit table | Datasheet or controls protection note | S11,S12
THM-03 | Thermal and qualification | A | Y | Provide the qualification basis for the offered build: IEC 61730, IEC 61215, IEC TS 63126 if applicable, and any technology-specific or in-house tests actually completed. | Qualification must attach to the actual offered product, not to a generic technology family. | Qualification matrix | Test reports, certificates, summary matrix | S08,S09,S10,S11 | A03
THM-04 | Thermal and qualification | A | Y | Provide evidence on humidity, condensation, seal durability, and moisture tolerance relevant to the blind chamber and electrical exits. | Moisture is an architecture-specific risk in enclosed moving PV assemblies. | Environmental test summary | Test report, climatic test matrix, inspection criteria | S13,S19 | A04,A05
THM-05 | Thermal and qualification | B | N | State whether thermography is recommended at factory acceptance, site acceptance, or in maintenance, and define the usable inspection conditions. | Closes the practical thermal-diagnostics pathway. | Inspection note | Thermography procedure or guidance | S20
THM-06 | Thermal and qualification | B | N | Provide any known installation conditions that materially increase temperature or invalidate the standard performance basis. | Needed to identify high-temperature trigger conditions early. | Constraint note | Application note, exclusions, thermal warnings | S11,S17
THM-07 | Thermal and qualification | B | N | Provide building-product fire or smoke related declarations that the façade team must account for, if applicable to the offered assembly. | Prevents a late handoff gap between PV and façade/fire reviewers. | Declaration set | Certificates, declarations, façade-system notes | S01,S02
REL-01 | Reliability and service | A | Y | Provide actuator cycle-life evidence under the actual load/environment envelope of the offered product. | Moving-element reliability is central and cannot be inferred from generic blind hardware. | Life-test summary | Qualification report, cycle-test report | S19
REL-02 | Reliability and service | A | Y | Provide evidence for cable/harness flex life or motion-fatigue control at all moving electrical interfaces. | Intermittent motion-related conductor failures are difficult to localize after installation. | Reliability summary | Motion-cycle test, bend-life data, design note | S13,S15,S19
REL-03 | Reliability and service | A | Y | Provide feedthrough and seal-interface reliability evidence under temperature cycling, humidity, and service handling. | This is one of the highest-risk latent-fault interfaces in the system. | Reliability summary | Test report, design verification plan, warranty note | S13,S19 | A05
REL-04 | Reliability and service | B | N | Provide field failure modes seen to date and the current corrective-action status for each significant mode. | Field feedback is often more informative than generic MTBF language. | Failure-mode table | NCR/CAPA summary, anonymized field data | S19
REL-05 | Reliability and service | B | N | Provide expected replacement times and special access needs for L1/L2/L3/L4 interventions. | Needed for downtime and access-cost modeling. | Service table | Service procedure, required tools, labor assumptions | S19 | A07,A10
REL-06 | Reliability and service | A | Y | Provide the actual replacement procedure for a failed unit, including electrical isolation steps, recommissioning checks, and risk of misconnection. | Service procedure quality is a major differentiator for enclosed façade hardware. | Procedure document | Replacement work instruction, recommissioning checklist | S06,S18,S19 | A07,A10
REL-07 | Reliability and service | B | N | Provide preventive-maintenance intervals, inspection points, consumables, and explicit no-maintenance claims or exclusions. | Needed to turn 'low maintenance' into an auditable O&M statement. | Maintenance schedule | Maintenance manual, warranty exclusions | S19 | A10
REL-08 | Reliability and service | B | N | Provide the spare-parts strategy and parts availability horizon for actuators, controllers, connectors, and special glass/blind subassemblies. | Long lead items drive lifecycle risk in façade retrofits. | Spares table | Part list, lead times, obsolescence policy | S19
COM-01 | Commissioning and handover | A | Y | Provide the standard commissioning package: single-line, labeling scheme, point list, acceptance tests, and record sheets. | This closes the IEC 62446-style handover gap before procurement. | Document set | Commissioning pack, templates, FAT/SAT forms | S18
COM-02 | Commissioning and handover | A | Y | State the required pre-energization, energization, and functional tests for first power-up and post-replacement recommissioning. | Needed for safe startup and clean service loops. | Test matrix | Commissioning procedure, replacement recommissioning steps | S18,S19 | A07
COM-03 | Commissioning and handover | A | Y | Provide acceptance limits or tolerances for key values: measured Voc, current, angle accuracy, telemetry availability, and temperature baseline. | Without pass/fail limits, a commissioning checklist is only paperwork. | Tolerance table | Acceptance criteria document | S18,S20 | A08
COM-04 | Commissioning and handover | B | N | Provide the required as-built labels and naming conventions for units, groups, feedthroughs, and control points. | Makes later diagnostics and part replacement tractable. | Naming convention table | Labeling standard, sample drawings | S18,S19
COM-05 | Commissioning and handover | B | N | Provide a sample event log or SCADA export showing normal operation, alarm behavior, and fault reset behavior. | Reduces ambiguity in monitoring/BMS integration. | Sample export | CSV/log export, screenshot, protocol map | S18,S19
COM-06 | Commissioning and handover | B | N | State training, witnessing, or vendor attendance requirements for FAT, SAT, first energization, and warranty-preserving maintenance. | These conditions can materially affect deployment cost and schedule. | Responsibility matrix | Commercial/technical terms, commissioning scope | S18,S19
BUS-01 | Commercial and warranty | B | N | Provide warranty terms by subsystem: glass, PV performance, blind mechanics, actuators, electronics, controls software, and connectors/feedthroughs. | Subsystem-split warranty terms matter more than a single headline number. | Warranty matrix | Warranty document, exclusions, transfer rules | S19 | A10
BUS-02 | Commercial and warranty | B | N | List warranty exclusions triggered by non-approved power electronics, control logic, mounting details, cleaning, or service practices. | Needed to keep architecture and O&M decisions contract-safe. | Exclusion list | Warranty conditions, approved-use matrix | S05,S19 | A10
BUS-03 | Commercial and warranty | B | N | Provide indicative lead times, minimum order conditions, and any long-lead custom parts relevant to pilot and scale-up deployment. | Directly affects roadmap realism and retrofit planning. | Commercial table | Offer conditions, supply-chain note | S19
BUS-04 | Commercial and warranty | B | N | Provide reference projects or pilot installations relevant to similar façade orientation, climate, and operational profile. | Useful for benchmarking and identifying hidden deployment constraints. | Reference list | Project list, contactability limits, installed dates | S17,S19
Note on K1: Vendor should answer here. Prefer document-backed response, not marketing text.
Note on L1: Reference the exact source document or drawing title.
Note on M1: Issue date or revision/date for traceability.
Note on N1: State whether the response is contractually binding or informational only.
Note on O1: Suggested entries: Yes / Partial / No.

## Closure_Map
Closure ID | Type | Statement | Questions covering it | Closure evidence required | Status | Owner | Notes
A03 | Assumption | Actual PV technology and stack used | ELE-01,ELE-02,THM-03 | Datasheet + qualification matrix + product revision statement
A04 | Assumption | Blind in main IGU cavity vs dedicated chamber | ARC-01,ARC-02,THM-01,THM-04 | Section drawing + chamber dimensions + environmental evidence
A05 | Assumption | Electrical feedthrough exits through frame edge | ARC-01,ELE-10,REL-03 | Section/detail drawing + feedthrough qualification
A06 | Assumption | Actuation architecture is local vs grouped | ARC-04,CTL-01,CTL-03 | Controls block diagram + actuator data
A07 | Assumption | Unit/group can be isolated and replaced without oversized outage | ARC-03,ELE-08,REL-05,REL-06,COM-02 | Single-line + isolation procedure + replacement work instruction
A08 | Assumption | Temperature sensing/observability exists or can be inferred credibly | CTL-02,THM-01,COM-03 | Point list + temperature evidence + acceptance limits
A09 | Assumption | Approved connector family and cable class exist for route/environment | DOC-05,ELE-10,ELE-11,ELE-12 | Connector/cable schedule + datasheets + route limits
A10 | Assumption | Low-maintenance claim does not eliminate defined service procedures | DOC-03,REL-06,REL-07,BUS-01,BUS-02 | Maintenance manual + replacement procedure + warranty exclusions
S01 | Design row | BIPV module as building product | DOC-01,ARC-01,THM-07 | Datasheet + section drawing + building-product declarations
S02 | Design row | BIPV system in building | ARC-01,ARC-02,ARC-05,THM-07 | Section/integration drawing + installation constraints
S03 | Design row | Array voltage envelope | ELE-01,ELE-03,ELE-04,ELE-06 | Unit ratings + subdivision + aggregation limits
S04 | Design row | Array current envelope | ELE-01,ELE-03,ELE-06 | Unit ratings + aggregation limits
S05 | Design row | MPPT compatibility and downstream topology | ELE-05,ELE-06,ELE-07,BUS-02 | IV/PV curves + allowed architectures + exclusions
S06 | Design row | Disconnect / isolation boundary | ELE-08,REL-06,COM-02 | Single-line + isolation procedure + recommissioning steps
S07 | Design row | Earthing / insulation monitoring | ELE-09,ELE-13 | Protection concept + BOS responsibilities
S08 | Design row | Module construction safety | ELE-02,THM-03 | Technology declaration + qualification basis
S09 | Design row | Module safety testing | ELE-04,THM-03 | Bypass topology + safety/qualification reports
S10 | Design row | Module design qualification | DOC-02,ELE-02,THM-03 | Revision delta + actual qualification evidence
S11 | Design row | High-temperature deployment trigger | ARC-02,THM-01,THM-02,THM-03,THM-06 | Thermal evidence + limits + qualification path
S12 | Design row | Integrated electronics near PV | DOC-05,ARC-04,ELE-07,ELE-09,CTL-01,CTL-03,THM-02 | BOM + architecture + protection + thermal limits
S13 | Design row | Junction / feedthrough interface | ELE-10,REL-02,REL-03,THM-04 | Feedthrough detail + reliability evidence
S14 | Design row | Connector suitability | ELE-11 | Connector schedule + mating rules
S15 | Design row | Cable suitability | ELE-12,REL-02 | Cable schedule + route/flex evidence
S16 | Design row | Performance parameter basis | DOC-01,ELE-01,ELE-05,THM-01 | Datasheet + IV/PV curves + thermal basis
S17 | Design row | Incidence-angle / operating-temperature basis | ARC-02,ARC-05,ELE-05,THM-01,BUS-04 | Geometry constraints + representative performance evidence
S18 | Design row | Commissioning docs and tests | DOC-03,ELE-08,CTL-02,CTL-07,COM-01,COM-02,COM-03,COM-04,COM-05,COM-06 | Commissioning pack + point list + event/acceptance data
S19 | Design row | Maintenance logic and serviceability | ARC-03,ARC-04,ARC-06,ELE-12,CTL-05,REL-01,REL-02,REL-03,REL-05,REL-06,REL-07,REL-08,BUS-01,BUS-02,BUS-03 | Replacement, maintenance, reliability, warranty evidence
S20 | Design row | Thermal inspection / diagnostic pathway | ELE-14,THM-05,COM-03,COM-05 | Fault signatures + thermography guidance + acceptance limits

## Scoring
ID | Section | Priority | Knockout | Weight | Completeness (0-5) | Evidence quality (0-5) | Technical adequacy (0-5) | Residual risk (0-5, higher=worse) | Weighted score | Knockout fail? | Reviewer decision | Reviewer notes
Summary
Total weighted score
Average weighted score
Knockout fails
Priority A rows unresolved
Note on J1: Formula: Weight × MAX(0, AVERAGE(Completeness, Evidence, Adequacy) - 0.5 × ResidualRisk)
Note on K1: Automatic knockout flag if a Knockout row has any core score below 3.