Step-by-Step Guide to Choosing the Most Suitable BIPV Architecture

Designing a photovoltaic system—especially for Building-Integrated Photovoltaics (BIPV) like Active Windows—requires a structured approach to balance energy harvest, safety, and cost. Here is a comprehensive, scratch-written methodology for selecting the ideal electrical connection topology.

Step 1: Define the Project Scope and Load Profile Begin by clearly defining the core objectives of the installation. Ascertain whether the system will be grid-tied, standalone, or a hybrid AC/DC microgrid. For a grid-tied system, the primary goal is often maximizing the energy yield (kWh/kWp) and utilizing the grid as a buffer, whereas standalone systems require careful load analysis to size battery storage adequately.

Step 2: Execute a Comprehensive Site and Shading Survey Because BIPV systems are integrated into building facades, they are highly susceptible to both near-field shading (from balconies, trees, or structural elements) and global/horizon shading (from neighboring buildings). Even if only a small percentage of a panel is shaded, power generation can drop by as much as 80% due to the series connection of cells. You must plot the sun's path across the sky throughout the year to identify the precise shading profile for the facade.

Step 3: Map the Viable Topologies Based on the project's scale, outline the potential electrical architectures. The main categories include:

- Centralized MPPT (CMPPT): Standard string systems where panels are wired in series to a single central inverter.

- Distributed MPPT (DMPPT) at the Module Level: This includes Microinverters (Module-Integrated Parallel Inverters) that convert DC to AC directly at the panel, or Power Optimizers (Module-Integrated Parallel/Series Converters) that regulate DC voltage at the panel level before sending it to a central inverter or DC bus.

Step 4: Conduct Technical Benchmarking for Shading Tolerance Evaluate how each topology handles the shading mapped in Step 2. In a CMPPT string system, a single shaded module forces the entire string's current to drop, creating severe mismatch losses and potential "hot spots". If the facade experiences complex shading, you must pivot to a DMPPT architecture (microinverters or optimizers) so that each window operates independently, isolating the performance drop to only the shaded windows.

Step 5: Perform a Multi-Criteria Decision Analysis (MCDA) Objectively evaluate the shortlisted topologies against strict project constraints:

- Electrical Safety: High-voltage DC strings in building facades pose a severe fire hazard from electric arcs that do not self-extinguish. Architectures utilizing module-level power electronics or a "DC bus per floor" can limit system voltage and mitigate these risks.

- Reliability: Distributed electronics (like microinverters) place sensitive components in harsh, high-temperature facade environments, which can shorten their lifespan.

- Economics: Balance the higher capital expenditure (CAPEX) and wiring complexity of distributed systems against the long-term energy yield gains.

Step 6: Verify Regulatory Compliance Ensure the chosen architecture complies with international and local building codes. This includes the National Electrical Code (NEC) Article 690 for PV systems, IEC standards for inverter safety (like IEC 62109), and vital safety functions like anti-islanding protection (UL 1741) to ensure the system safely disconnects during a power outage.

Step 7: Draft the Technical Requirements Specification (TRS) Finalize the selection and document the engineering baseline. This document must define the voltage levels, specific connector standards, wiring topology, Building Management System (BMS) integration protocols, and the real-time monitoring architecture required for the chosen system.

Architecture Selection Checklist

1. Site & Shading Analysis

- [ ] Has a detailed shading analysis (near-field and horizon) been completed?

- [ ] Have the orientation and tilt (or vertical facade angle) been factored into the energy yield calculations?

- [ ] Is the shading severe enough to mandate a Distributed MPPT (DMPPT) architecture?

2. Electrical Configuration

- [ ] Is the system grid-tied, off-grid, or utilizing a hybrid AC/DC microgrid?

- [ ] What are the maximum allowable DC voltage limits for the building facade?

3. Topology Evaluation (MCDA)

- [ ] CMPPT (String Inverter): Ruled out if partial shading or high-voltage DC routing in the facade is an issue?

- [ ] MIPI (Microinverters): Selected if modularity, AC safety, and individual panel tracking are prioritized, and higher CAPEX is acceptable?

- [ ] MIPC/MISC (Power Optimizers): Selected if utilizing a DC-bus-per-floor approach or integrating with DC battery storage?

4. Safety & Regulatory Compliance

- [ ] Does the system include DC arc-fault detection and limit high-voltage DC hazards?

- [ ] Are all components (panels, inverters, cables) certified to relevant IEC/UL/NEC standards?

- [ ] Does the inverter include anti-islanding protection?

5. Reliability & Economics

- [ ] Has environmental stress testing been considered for electronics placed within the hot facade environment?

- [ ] Are the installation time, wiring complexity, and CAPEX within the project's acceptable thresholds?

- [ ] Have standard protocols (e.g., KNX, Modbus) been selected for BMS monitoring integration?